## BLANK BOQ
[Bidder's Letterhead]
[Date]
To: Tarlac State University
Re: Invitation to Bid No.
BILL OF QUANTITIES
Item No. | Work Description | Materials |  | Work Item |  | Direct Cost | Indirect Cost | Total Direct & Indirect Cost | Value Added Tax | Total Cost | Cost per Unit of Work Item
|  | Quantity | Unit | Quantity | Unit | Materials, Labor, and Equipment | Overhead, Contingencies, Miscellaneous, & Profit
(1) | (2) |  |  | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10)
1 | General Requirements
1.1 | Mobilization & Demobilization |  |  | (3): 1; (4): lot
1.2 | Construction Occupational Safety & Health |  |  | (3): 1; (4): lot
1.3 | Temporary Facilities, Billboard and Barricade |  |  | (3): 1; (4): lot
1.4 | Testing and commissioning for fire pump assembly (including Pressure and Leak Testing of Pipes) |  |  | (3): 1; (4): lot
Sub-Total
2 | Mechanical Works
2.1 | Fire Pump System |  |  | (3): 1; (4): lot
2.1.1 | UL/FM Vertical Turbine Electric-Driven: 400GPM @ 80PSI, 30HP/60HZ/ 230V/ 3PH, with Control Panel, Air Relief Valve (UL/ FM), Circulation Safety Valve (UL/FM), Pump Outlet Gauges | 1 | set
2.1.2 | Submersible Jockey Pump: 15GPM @ 90PSI, 2HP/ 60HZ/ 230V/3PH, with Control Panel | 1 | set
2.2 | Fire Pump Valves and Accessories |  |  | (3): 1; (4): lot
2.2.1 | OS & Y Gate Valve, 100mm Ø, UL/FM | 2 | pc
2.2.2 | Supervisory Switch, UL/FM | 2 | pc
2.2.3 | Rubber Expansion Joint, 100mm Ø (for Fire Pump Discharge) | 1 | pc
2.2.4 | Check Valve 100mm Ø, UL/FM (for Fire Pump Discharge) | 2 | pc
2.2.5 | Gate Valve 40mm Ø, UL/FM (for Jockey Pump Discharge) | 1 | pc
2.2.6 | Check Valve 40mm Ø (for Jockey Pump Discharge) | 1 | pc
2.2.7 | Alarm Check Valve 100mm Ø, UL/FM | 1 | pc
2.2.8 | Flow Meter 100mm Ø, UL/FM (for Fire Pump Test Line) | 1 | pc
2.2.9 | Fire Protection Pressure Relief Valve 100mm Ø, UL/FM | 1 | pc
2.3 | Floor Control Assembly
2.3.1 | OS & Y Gate Valve 80mm Ø, UL/FM | 5 | pc
2.3.2 | Supervisory Switch, UL/FM | 5 | pc
2.3.3 | Waterflow Switch 80mm Ø, UL/FM | 5 | pc
2.3.4 | Gate Valve 25mm Ø, UL/FM | 5 | pc
2.3.5 | Sight Glass, 25mm Ø | 5 | pc
2.3.6 | Gate Valve 50mm Ø, UL/FM | 5 | pc
2.3.7 | Pressure Gauge | 5 | pc
2.4 | Stand Pipe |  |  | (3): 1; (4): lot
2.4.1 | Fire Hose Valve 65mm Ø | 16 | pc
2.4.2 | Fire Department Connection 65mm Ø x 65mm Ø x 100mm Ø, UL/FM | 5 | pc
2.4.3 | Indoor Fire Hose Cabinet, Surfaced Type, Complete with 40mm Ø Angle Hose Valve, 40mm Ø Hose Nozzle, 40mm Ø x 30m Fire Hose Double Jacket and, and Hose Rack | 16 | set
2.5 | Inspector's Test Connection |  |  | (3): 1; (4): lot
2.5.1 | Sight Glass, 25mm Ø | 5 | pc
2.5.2 | Gate Valve 25mm Ø, UL/FM | 5 | pc
2.6 | Pipes and Fittings |  |  | (3): 1; (4): lot
2.6.1 | 100mm Ø, Black Steel Pipe Sch.40 Seemless Plain Ends ASTM A53 Gr. B 6m | 38 | pc
2.6.2 | 80mm Ø, Black Steel Pipe Sch.40 Seemless Plain Ends ASTM A53 Gr. B 6m | 125 | pc
2.6.3 | 65mm Ø, Black Steel Pipe Sch.40 Seemless Plain Ends ASTM A53 Gr. B 6m | 29 | pc
2.6.4 | 50mm Ø, Black Steel Pipe Sch.40 Seemless Plain Ends ASTM A53 Gr. B 6m | 15 | pc
2.6.5 | 40mm Ø, Black Steel Pipe Sch.40 Seemless Plain Ends ASTM A53 Gr. B 6m | 6 | pc
2.6.6 | 32mm Ø, Black Steel Pipe Sch.40 Seemless Plain Ends ASTM A53 Gr. B 6m | 288 | pc
2.6.7 | 25mm Ø, Black Steel Pipe Sch.40 Seemless Plain Ends ASTM A53 Gr. B 6m | 94 | pc
2.6.8 | Fittings, Sch.40, Black Steel (Elbow Standard,Tee Straight,Tee Reducer,Concentric Reducer,Eccentric Reducer, Grooved Fittings,Slip On Flange,Blind Flange,B.I. End Cap and Etc.) | 1 | lot
2.6.9 | Pipe Hangers, Supports and Sleeves | 1 | lot
2.6.10 | Epoxy Enamel Paint for Steel Pipes (including surface preparation, primer and 2 top coats and primer) | 1 | lot
2.7 | Sprinklers Heads, FHCs, and Accessories |  |  | (3): 1; (4): lot
2.7.1 | K = 5.6, Quick Response, 155°F, 1/2" NPT, Pendent Type w/ escutcheon plate | 12 | pc
2.7.2 | Indoor Fire Hose Cabinet, Surfaced Type, Complete with 40mm Ø Angle Hose Valve, 40mm Ø Hose Nozzle, 40mm Ø x 30m Fire Hose Double Jacket and, and Hose Rack | 20 | set
3 | Structural Works
3.1 | Concrete and Steel Works |  |  | (3): 1; (4): lot
3.1.1 | Excavation | 1167.936 | m³
3.1.2 | Concrete 3000 psi | 70.4088 | m³
3.1.3 | Reinforcement
3.1.3.1 | 16mm ∅ x 6m DSB Grade 40 | 3227.466 | kg
3.1.3.2 | 12mm ∅ x 6m DSB Grade 40 | 1083.5132 | kg
3.1.3.3 | 10mm ∅ x 6m DSB Grade 40 | 335.2778 | kg
3.1.4 | #16 GI Tie Wire | 78 | kg
3.1.5 | 20 mm ∅ Stainless Steel Bar Ladder Rung | 9 | pc
3.2 | Roof Framing |  |  | (3): 1; (4): lot
3.2.1 | 2" x 4" x 1.5 mm thk. G.I. Tubulars | 5 | pc
3.2.2 | 2" x 4" x 1.5 mm thk. G.I. C- Purlins | 10 | pc
3.2.3 | 2" x 10" x 1.5 mm thk. G.I. C- Purlins | 4 | pc
3.2.3 | 1 1/2" x 1 1/2" x 3.5 mm thk. Anglebar | 1 | pc
3.2.3 | 10mm ∅ Round Bar | 2 | pc
3.2.4 | Epoxy Primer Paint for Steel Framing | 1 | lot
3.2.5 | Welding Rods | 1 | lot
4 | Architectural Works
4.1 | Masonry and Plastering Works |  |  | (3): 1; (4): lot
4.1 | 4" CHB Wall (including mortar and 10 mm steel reinforcement every three CHB layer and 0.60 m horizontal spacing) | 46.92 | m²
4.2 | Cement Plastering of Interior and Exterior Walls, Column, Beams, etc. | 89.42 | m²
4.2 | Roofing Materials |  |  | (3): 1; (4): lot
4.2.1 | 0.50 mm thk. Prepainted Rib Type Roofing | 34 | m
4.2.2 | 0.50 mm thk. Prepainted Roof Flashing | 9 | m
4.2.3 | 0.50 mm thk. Prepainted Roof Gutter | 3 | m
4.2.4 | 10 mm thk. Aluminum Fim Laminated Foam Two Sided w/ 12.5 mm welded wire #21 | 34 | m²
4.2.5 | Tekscrew,Blind Rivets,Sealant, etc. | 1 | lot
4.3 | Floor Finishing Works |  |  | (3): 1; (4): lot
4.3.1 | Smooth Cement Floor Finish | 14.61 | m²
4.4 | Ceiling Works |  |  | (3): 1; (4): lot
4.4.1 | 6" x 0.50 mm Pre- Painted Metal Spandrel including air ventilation holes, mouldings and framing system | 20 | m²
4.5 | Painting and Water Proofing Works |  |  | (3): 1; (4): lot
4.5.1 | Semi-Gloss Latex Paint Finish on Exterior and Interior Wall, Beams, Columns, Ledges, etc. (surface preparation, primer and 2 top coats) | 89.42 | m²
4.5.2 | Waterproofing of inside perimeter wall and floor (surface preparation, appplication of 5 coats of cementitious waterproofing) | 75.24 | m²
4.6 | Doors |  |  | (3): 1; (4): lot
4.6.1 | D1 - Doubel Swing Steel Louver Door with Metal Door Jamb and Complete Accessories | 1 | set
4.7 | Windows |  |  | (3): 1; (4): lot
4.7.1 | W1 - Steel Louvered Window with Tubular Steel Framing | 1 | set
4.7.2 | W2- Steel Louvered Window with Tubular Steel Framing | 1 | set
5 | Plumbing Works
5.1 | Stormdrain, Downspout and Fittings |  |  | (3): 1; (4): lot
5.1.1 | 75 mm Ø S1000 PVC Pipe | 4 | pc
5.1.2 | 75 mm Ø Elbow PVC | 6 | pc
5.1.3 | 75 mm Ø Aluminum Downspout Strainer | 2 | set
5.1.4 | 75 mm Ø HDPE Pipe for CisternWater Supply Line | 130 | m
5.1.5 | 75 mm Ø Heavy Duty Brass Body Water Meter | 1 | pc
5.1.6 | 75 mm Ø Heavy Duty Brass Body Gate Valve | 2 | pc
5.1.7 | 76 mm Ø Heavy Duty Brass Body Check Valve | 1 | pc
5.1.8 | 77 mm Ø Heavy Duty Brass Body Float Valve | 1 | pc
5.1.9 | Assorted Fittings and Accessories | 1 | lot
6 | Electrical Works
6.1 | Lighting, Power and Fire Pump System |  |  | (3): 1; (4): lot
6.1.1 | 36W Linear LED Pendant Light [Color: Daylight¦ Black Housing] | 4 | set
6.1.2 | 12W Surface Mounted LED Panel Light [Color: Daylight] | 5 | set
6.1.3 | Universal Duplex Convenience Outlet | 2 | set
6.1.4 | 2 Gang Switch Wide Series with LED | 1 | set
6.1.5 | 2" x 4" GI Utility Box with Connector and Cover | 2 | set
6.1.6 | 4" x 4" GI Junction Box with Connector and Cover | 4 | set
6.1.7 | Fire Pump Room Panel (Bolt-on) Main: 250AT 3P MCCB Branch: 1-450AT 3P MCCB, 1-60AT 3P MCCB, 1-30AT 3P MCCB, 2-20AT 2P MCCB Space: 0 With Busbars and Terminal Lugs Nema-1 Enclosure | 1 | set
6.1.8 | 12 inche x 12 inches x 4 inches (L x W x D) GA 16 Metal Pull Box | 5 | set
6.1.9 | 3" Ø RSC | 40 | pc
6.1.10 | 1 1/2" Ø RSC | 2 | pc
6.1.11 | 3/4" Ø RSC | 2 | pc
6.1.12 | 1/2" Ø RSC | 15 | pc
6.1.13 | 1 1/2" Ø LFMC | 8 | m
6.1.14 | 3/4" Ø LFMC | 10 | m
6.1.15 | 1/2" Ø Mica Tube | 10 | m
6.1.16 | 100 mm² Cu. THHN/THWN (STR) | 375 | m
6.1.17 | 30 mm² Cu. THHN/THWN (STR) | 50 | m
6.1.18 | 5.5 mm² Cu. THHN/THWN (STR) | 25 | m
6.1.19 | 3.5 mm² Cu. THHN/THWN (STR) | 1 | box
6.1.20 | 10' Ground rod with solderless connector | 1 | lot
6.1.21 | Conduit Support, Connector and Hanger (Elbow, Box Connector, Angle Bar, U-Bolt, Dynabolt with nut and washer) | 1 | lot
| Total Bid Price | [In Words] |  | (9): [In Figures]
[Signature]
[Name of Authorized Signatory]
[Position/Title]